## Slide 1: Risk Assessment and Ventilation Modeling for Hydrogen Vehicle Repair Garages
Brian Ehrhart, Shaun Harris, Myra Blaylock, Alice Muna, Spencer Quong (QAI), Dany Oliva (TMNA)
Sandia National Laboratories
This presentation does not contain any proprietary, confidential, or otherwise restricted information
Paper # 236
SAND2019-10691 C
Sandia National Laboratories is a multimission laboratory managed and operated by National Technology & Engineering Solutions of Sandia, LLC, a wholly owned subsidiary of Honeywell International, Inc., for the U.S. Department of Energy’s National Nuclear Security Administration under contract DE-NA0003525.
International Conference on Hydrogen Safety
September 24, 2019

## Slide 2
Demand for additional maintenance facilities grows with increased hydrogen fuel cell electric vehicle (FCEV) use
Purpose-built, new infrastructure is expensive
Ventilation and other upgrades required for existing facilities
  Cost can be very high for large, multi-bay repair facilities
Objective: Perform application-specific risk analyses to identify credible hazard scenarios resulting in unintentional indoor releases of hydrogen during vehicle maintenance operations, characterize key hydrogen release scenarios through detailed modeling, and improve code requirements.
H2 Vehicle Repair Garage Infrastructure

## Slide 3: Approach: Risk Analysis and Modeling to Inform Code Requirements
Risk Analysis
  Repair garage application-specific risk assessment and credible scenario identification
Modeling
  Computational fluid dynamics (CFD) modeling for indoor hydrogen releases
  Based on key scenarios from risk assessment
Code Recommendations
  Results of risk analyses and modeling will be incorporated into proposals to improve requirements for repair garages while maintaining same level of safety
Select part
Identify relevant maintenance activities
Identify potential issues
Apply risk value

## Slide 4: HAZOP Risk Analysis
Hazard and Operability Study (HAZOP)
  Develop framework with input from QAI and industry for H2 FCV scenarios
  Scenarios ranked by severity of consequence and frequency of occurrence
490 unique scenarios identified
  18 of these had potential hydrogen release
  Others eliminated due to equivalent or lesser concern
Severity Value | Description
3 | Major: Release of full inventory of hydrogen
2 | Moderate: 1 tank of hydrogen (half of full inventory)
1 | Minor: Small release of hydrogen
Frequency Value | Description | Frequency
5 | Intentional | 
4 | Anticipated | f > 10-2/year
3 | Unlikely | 10-4/yr < f < 10-2/yr
2 | Extremely unlikely | 10-6/yr < f < 10-4/yr
1 | Beyond extremely unlikely | f < 10-6/yr

## Slide 5: HAZOP Scenarios: 4 Medium-Risk, No High-Risk
Scenario | Event Description | Consequence (Release) | Comments
A | External fire causes TPRD release of H2 cylinders | 2 tanks, high pressure, jet fire (worst consequence) | Only occurs when external fire heats H2 storage
B | Small release in low-pressure system | <1 tank, low pressure (most likely) | Mitigated by detection; the event below bounds this scenario
C | Premature disconnect of venting tool | 1 or 2 tanks, low pressure | Focus of modeling due to higher risk score (combination of likelihood and consequence)
D | Premature disconnect of high pressure defueling tool | 1 tank, high pressure | Low probability of occurring

## Slide 6: CFD Modeling Domain
Event: Vent hose severed while vehicle defueling to an external exhaust outlet
Typical 12-bay garage
  Each bay 14’ x 27’ x 16’
  Center aisle 6’ x 84’ x 16’
Leak:
  2.5 kg of H2 released
    Most hydrogen vehicles have 2 tanks which store approximately 2.5 kg of hydrogen each
  Release from mid-pressure port: 1.5 MPa (217.6 psi)
    Downward release from vehicle underside

## Slide 7: Modeling Scenarios Analyzed
Facility ventilation varied between cases
  No ventilation
  Regular ventilation (1 cfm/ft2) near the vehicle
  Regular ventilation (1 cfm/ft2) away from the vehicle
  Higher ventilation (300 cm/s) directed at the vehicle
Computer modeling simulates the leak and shows:
  Direction of ventilation and released gas
  Any areas of flammable mixture (Lower Flammability Limit (LFL) = 4 mol%)
Total flammable mass is critical safety metric considered

## Slide 8: Hydrogen Leak Velocity
CFD simulations rely on low-velocity gas flow
Flammable concentration does not reach floor for low-pressure release
  May need to model differently for high-pressure releases in the future

## Slide 9: No Ventilation
Flammable Area
(2 g total flammable H2)
Vehicle
Maximum flammable mass scenario
Leak comes from center of bottom of vehicle
Blue walls and floor are 0 cm/s velocity
Showing no air movement for no-ventilation scenario
Flammable area has color-scale based on concentration
Fraction of LFL

## Slide 10: Ventilation Near Leak
Vent Outlets
Vent Air Inlet
(4 inlets, 1 cfm/ft2)
Flammable Area
(0.4 g total flammable H2)
Smaller than no-ventilation scenario
Vehicle
Ventilation directed at leak area leads to a decrease in maximum flammable mass
Yellow on walls and floor means ≥100 cm/s velocity
Showing air movement from ventilation
Flammable area has color-scale based on concentration
Fraction of LFL

## Slide 11: Ventilation Near Leak (Again) – Showing Dissipation
Vent Air Inlet
(4 inlets, 1 cfm/ft2)
Vehicle
Side view of leak scenario
Green is flammable area near leak point
Purple is hydrogen concentration below LFL
Hydrogen mixes with air (diluting) and going towards ceiling vent outlets
Fraction of LFL

## Slide 12: Ventilation Away From Vehicle
Vent Outlets
Vent Air Inlet
(4 inlets, 1 cfm/ft2)
Flammable Area
(2 g total flammable H2)
Similar to no-ventilation case
Vehicle
Ventilation away from the vehicle has little affect on maximum flammable mass
Yellow on walls and floor mean ≥100 cm/s velocity
Showing air movement from ventilation
Fraction of LFL

## Slide 13: Higher Ventilation Directed at Vehicle
Vent Outlets
Vent Air Inlet
(1 inlet higher velocity
Total: 1 cfm/ft2)
Flammable Area
(0.06 g total flammable H2)
Smaller than ventilation-near-leak and no-ventilation scenarios
Vehicle
Higher ventilation directed at the leak area leads to the largest decrease of flammable mass
Dark yellow shows 300 cm/s velocity.
Showing air movement from ventilation
Fraction of LFL

## Slide 14: Hazard Quantification
Flammable mass
  Total flammable mass of hydrogen in garage based on wherever the local hydrogen concentration is >LFL (>4 mol%)
No-ventilation case has low amount of flammable mass relative to mass released (<0.1% of 2.5 kg)
  Dispersion of hydrogen in large area
  Slow (low pressure) release
Ventilation directed at leak area leads to a 80% to 97% decrease in maximum flammable mass
Ventilation not directed at leak has little effect on maximum flammable mass
Ventilation | Maximum Flammable Mass (g)
No Ventilation | 2
Standard ventilation near leak | 0.4
Standard ventilation away from leak | 2
Higher velocity ventilation near leak | 0.06
1,000 g of hydrogen ≈ 1 gallon of gasoline

## Slide 15: Conclusions
Code-compliant ventilation might not reduce flammable mass compared to no-ventilation case
  Flammable mass small relative to amount released for low-pressure leak
Ventilation directed at leak reduced flammable mass by an order-of-magnitude
Higher velocity, directed ventilation further reduces flammable mass
  Might provide a way to increase safety without changes to entire facility

## Slide 16: Remaining Challenges
  Risk analysis and modeling performed for large repair garage
    Other structures (parking, small garages) could have different hazards and geometries
  Effect of spreading or obstructions
    Current CFD modeling jet unaffected by wall, floor, equipment, etc.
  Further incorporation of results into safety codes and standards
    Results and recommendations need to be translated into improved code requirements that maintain same level of safety

## Slide 17: Questions?
Thank you!